## June 2023
Metro Vancouver - Waste-to-Energy Facility
CONTINUOUS EMISSION MONITORING SYSTEM
June 2023
1. Monthly Summary Report
Parameter | Compliance Limit (mg/dscm) | Compliance Period | Maximum Measurement (mg/dscm)
|  |  | Unit 1 | Unit 2 | Unit 3
CO | 50 | 24 hr | 45.4 | 37.8 | 40
HCl | 55 | 1 hr(2)
SO2 | 200 | 24 hr | 83.7 | 124.3 | 85
NOx | 190 | 24 hr | 132.7 | 135.6 | 139.4
THC | 10 | 24 hr | 0.17 | 0.47 | 1.79
Monthly Average (mg/dscm)
|  |  | Unit 1 | Unit 2 | Unit 3
Opacity (%) |  |  | 0.42633 | 1.1434 | 0.61231
CO |  |  | 35.2033 | 29.0517 | 34.2077
THC |  |  | 0.071333 | 0.067241 | 0.56808
SO2 |  |  | 48.4367 | 64.2379 | 55.5769
NOx |  |  | 126.6967 | 128.8034 | 132.5846
THC
Interim Discharge Limits will apply until and including the following dates, at which point the Discharge Limits and Response Limits will apply
a. HCl – March 3, 2025 |  |  | b. SO2 – March 3, 2025
* Metro Vancouver has confirmed with Covanta that the equipment is calibrated on a daily basis, and is within range.
2. Monthly Exceedance Report
2.a. Discharge Limit Exceedances
Unit | Compliance Parameter |  | Discharge Limit (mg/dscm) | Date | Exceedance Level
Reason/Action Taken
2.b. Response Limit Exceedances
Compliance Parameter: Total Hydrocarbons
Response Limit: 20 mg/dscm 1/2 hour average
Date / Time | Duration | Exceedance (mg/dscm) | Action Taken
Compliance Parameter: Carbon Monoxide
Response Limit: 100 mg/dscm 1/2 hour average
Unit No. 1
Date / Time | Duration | Exceedance (mg/dscm) | Action Taken
2023-06-01 09:30 | 30 min | 103.1 | Started gas burners, adjusted airflow, modified feed rate.
2023-06-07 11:30 | 30 min | 152.1 | Started gas burners, adjusted airflow, modified feed rate.
2023-06-20 04:30 | 30 min | 131.5 | Started gas burners, adjusted airflow, modified feed rate.
2023-06-22 10:00 | 30 min | 144.9 | Started gas burners, adjusted airflow, modified feed rate.
30 min
30 min
30 min
2022-04-23 20:00 | 30 min | 129 | Volatile fuel. Started gas burners, adjusted airflow, modified feed rate.
2022-04-24 13:00 | 30 min | 150.1 | Started gas burners, adjusted airflow, modified feed rate, checked instrumentation.
2022-04-27 09:00 | 30 min | 112 | Started gas burners, adjusted airflow.
2022-04-29 22:00 | 30 min | 126.3 | Started gas burners, adjusted airflow, modified feed rate, checked instrumentation.
2022-04-29 11:30 | 30 min | 122 | Started gas burners, adjusted airflow, modified feed rate, checked instrumentation.
2021-02-22 22:30 | 30 min | 140.3 | Started gas burners, adjusted airflow, modified feed rate, checked instrumentation.
| 30 min | 127 | Started gas burners, adjusted airflow, modified feed rate.
30 min
2021-04-28 14:00 | 30 min | 125.6 | Started gas burners, adjusted airflow, modified feed rate.
2023-06-30 15:30 | 30 min | 157.2 | Started gas burners, adjusted airflow, modified feed rate.
Compliance Parameter: Carbon Monoxide
Response Limit: 100 mg/dscm 1/2 hour average
Unit No. 2
Date / Time | Duration | Exceedance (mg/dscm) | Action Taken
2023-06-06 05:00 | 30 min | 120.9 | Started gas burners, adjusted airflow, modified feed rate.
2023-06-06 15:00 | 60 min | 112.5 | Feeder hang up. Started gas burners, adjusted airflow, modified feed rate.
2023-05-03 16:00 | 30 min | 115.8 | Started gas burners, adjusted airflow, modified feed rate, checked instrumentation.
2023-06-30 08:30 | 30 min | 146.3 | Started gas burners, adjusted airflow, modified feed rate.
2023-06-30 18:00 | 30 min | 118.7 | Adjusted airflow, modified feed rate.
2021-04-16 08:30 | 30 min | 212 | Started gas burners, adjusted airflow, modified feed rate.
2021-04-17 14:00 | 30 min | 235.2 | Started gas burners, adjusted airflow, modified feed rate.
2021-04-20 22:00 | 30 min | 109.3 | Feed chute lift, started gas burners, adjusted airflow, modified feed rate.
2021-04-22 11:00 | 30 min | 153.9 | Started gas burners, adjusted airflow, modified feed rate, checked instrumentation.
2021-04-24 17:30 | 30 min | 137.4 | Started gas burners, adjusted airflow, modified feed rate.
2022-04-19 09:00 | 30 min | 113.8 | Power interruption. Started gas burners, adjusted airflow, modified feed rate.
Compliance Parameter: Carbon Monoxide
Response Limit: 100 mg/dscm 1/2 hour average
Unit No. 3
Date / Time | Duration | Exceedance (mg/dscm) | Action Taken
2023-06-07 13:00 | 60 min | 156.6 | Online boiler wash. Started gas burners, adjusted airflow, modified feed rate.
2023-06-07 15:00 | 30 min | 262 | Online boiler wash. Started gas burners, adjusted airflow, modified feed rate.
2023-06-19 06:00 | 30 min | 117.3 | Started gas burners, adjusted airflow, modified feed rate.
2023-05-07 02:00 | 30 min | 191.7 | Adjusted airflow.
2023-05-07 06:30 | 30 min | 142 | Started gas burners, adjusted airflow.
2023-05-09 05:00 | 30 min | 127.2 | Feeder hangup. Started gas burners, adjusted airflow, modified feed rate.
2023-05-11 06:00 | 30 min | 186.7 | Started gas burners, adjusted airflow, modified feed rate.
2023-05-11 07:30 | 30 min | 124.5 | Started gas burners, adjusted airflow, modified feed rate.
2023-05-15 05:30 | 30 min | 163.3 | Started gas burners, adjusted airflow, modified feed rate.
2023-05-26 10:30 | 30 min | 112.2 | Started gas burners, adjusted airflow, modified feed rate, checked instrumentation.
2023-05-27 08:00 | 30 min | 174.8 | Turbine trip. Started gas burners, adjusted airflow, modified feed rate.
30 min
30 min
30 min
30 min
2023-06-30 08:30 | 30 min | 137.2 | Started gas burners, adjusted airflow, modified feed rate.
Compliance Parameter: Nitrogen Oxide
Response Limit: 350 mg/dscm 1/2 hour average
Unit No. 2
Date / Time | Duration | Exceedance (mg/dscm) | Action Taken
2021-03-01 22:00 | 30 min | Instrument Error | CEMS Failure, instrument reading showed erroneous 10,000 mg/dscm
2021-12-17 04:00 | 30 min | 438.2 | Shutdown, checked aqueous ammonia flow, checked low NOx system air flow, checked aqueous ammonia spray nozzle pattern, checked instrumentation.
Compliance Parameter: Opacity
Response Limit: 5% 1/2 hour average
Unit No. 3
Date / Time | Duration | Exceedance (mg/dscm) | Action Taken
2019-05-17 20:30 | 30 min | 14.05 | Visually inspected stack, purple plume, dissipated within 15 min.
Compliance Parameter: Total Hydrocarbons
Response Limit: 20 mg/dscm 1/2 hour average
Unit No. 3
Date / Time | Duration | Exceedance (mg/dscm) | Action Taken
2023-06-01 09:00 | 30 min | 33.34 | Monitored CO, checked instrumentation.
2019-11-01 14:30 | 30 min | 110.5 | Started gas burners, adjusted airflow, modified feed rate.
2019-10-29 09:00 | 30 min | 106.2 | Started gas burners, adjusted airflow.
2019-09-30 20:30 | 30 min | 110.3 | Started gas burners, adjusted airflow, modified feed rate.
2019-08-12 01:00 | 30 min | 120.3 | Started gas burners, adjusted airflow, modified feed rate.
2019-08-12 14:00 | 30 min | 117.8 | Feeder hang up, started gas burners, adjusted airflow, modified feed rate, cleared hang up.
2019-08-14 07:30 | 30 min | 133.6 | Started gas burners, adjusted airflow, modified feed rate.
2019-08-14 08:00 | 30 min | 374.8 | Started gas burners, adjusted airflow, modified feed rate.
2019-08-17 19:00 | 30 min | 135.1 | Started gas burners, adjusted airflow, modified feed rate.
2019-08-18 11:00 | 30 min | 117.1 | Spike during start-up. Gas burners already on, adjusted airflow and modified feed rate. Checked instrumentation.
2019-08-20 15:00 | 30 min | 110.2 | Adjusted airflow, modified feed rate.
2019-08-22 17:00 | 30 min | 160.9 | Feeder hang up, started gas burners, adjusted airflow, modified feed rate, cleared hang up.
2020-12-12 12:30 | 30 min | 34.41 | Monitored carbon monoxide, checked instrumentation. CEMS in maintenance mode.
2.c. Transient Conditions
Gas burners unavailable during shutdown and furnace temperature average below 800C
Unit | Duration | Date | Time
Cause
Action Taken to Restore Steady State Conditions
Remedial Action Planned and/or Taken
Gas burners unavailable during shutdown and furnace temperature average below 800C
Unit | Duration | Date | Time
#3 | 11 minutes | April 30 2022 | 16:40-16:51
Cause
Auxiliary burners on unit 3 were unavailable to maintain the secondary combustion zone temperature during boiler shutdown period. Unit 3 was placed in shutdown mode at 2022-04-30 16:40 due to an induced draft fan trip. The Provincial Boiler Vessel Safety Act and the Provincial Gas Act require a boiler purge following the restart of the combustion fans. The auxiliary burners were unavailable for a period of 11 minutes between 2022-04-30 16:40 and 2022-04-30 16:51.
Action Taken to Restore Steady State Conditions
Covanta started the induced draft fan at 2022-04-30 16:45. The natural gas burners were back online at 2022-04-30 16:51. The shutdown was completed at 2022-04-30 17:19.
Remedial Action Planned and/or Taken
An electrical braking system will be installed in the induced draft fan's variable frequency drive to prevent high voltage trips.
Gas burners unavailable during shutdown and furnace temperature average below 800C
Unit | Duration | Date | Time
#3 | 48 minutes | 2021-03-26 | 06:48-07:36
Cause
Auxiliary burners on unit 3 were unavailable to maintain the secondary combustion zone temperature during boiler shutdown period. Unit 3 was placed in shutdown mode at 2021-03-26 06:48 due to a BC Hydro power outage. The Provincial Boiler Vessel Safety Act and the Provincial Gas Act require a boiler purge following the restart of the combustion fans. The auxiliary burners were unavailable for a period of 48 minutes between 2021-03-26 06:48 and 2021-03-26 07:36.
Action Taken to Restore Steady State Conditions
Covanta restarted the induced draft fan at 2021-03-26 06:48. The natural gas burners were back online at 2021-03-26 07:36. The shutdown was completed at 2021-03-26 07:47.
Remedial Action Planned and/or Taken
None
Gas burners unavailable and unable to close feed chute damper during shutdown
Unit | Duration | Date | Time
2 | 46 min | 2020-11-04 | 21:11-21:57
Cause
Auxiliary burners on unit 2 were unavailable, due to a safety permissive, to maintain the secondary combustion zone temperature during a boiler shutdown period as required. The operator was unable to close the feed chute damper during the shutdown as required. Unit 2 was placed in shutdown mode at 2020-11-04 21:11 following an induced draft fan and forced draft fan trip. The operator was unable to close the feed chute damper as the refuse was above the damper in the feed chute. The Provincial Boiler Pressure Vessel Safety Act and the Provincial Gas Act required a boiler purge following the restart of the fans as the boiler temperature was below the safety permissive. The auxiliary burners were unavailable for a period of 22 minutes between 2020-11-04 21:11 and 2020-11-04 21:33.
Action Taken to Restore Steady State Conditions
Covanta restarted the induced draft fan at 2020-11-04 21:18 and the forced draft fan at 2020-11-04 21:18. The natural gas burners were back online at 2020-11-04 21:33. The shutdown was completed at 2020-11-04 21:57.
Remedial Action Planned and/or Taken
Metro Vancouver’s facility operator Covanta is checking all relays and wiring associated with the induced draft to identify what is causing the induced draft fan to trip.
Gas burners unavailable and unable to close feed chute damper during shutdown
Unit | Duration | Date | Time
2 | 1 hr 4 min | 2020-11-20 | 13:20-14:24
Cause
Auxiliary burners on unit 2 were unavailable, due to a safety permissive, to maintain the secondary combustion zone temperature during a boiler shutdown period as required. The operator was unable to close the feed chute damper during the shutdown as required. Unit 2 was placed in shutdown mode at 2020-11-20 13:20 following an induced draft fan and forced draft fan trip. The operator was unable to close the feed chute damper as the refuse was above the damper in the feed chute. The Provincial Boiler Pressure Vessel Safety Act and the Provincial Gas Act required a boiler purge following the restart of the fans as the boiler temperature was below the safety permissive. The auxiliary burners were unavailable for a period of 50 minutes between 2020-11-20 13:20 and 2020-11-20 14:10.
Action Taken to Restore Steady State Conditions
Covanta restarted the induced draft fan at 2020-11-20 13:21 and the forced draft fan at 2020-11-20 13:28. The natural gas burners were back online at 2020-11-20 13:38. The induced draft fan and forced draft fans tripped again at 2020-11-20 13:46 which tripped the natural gas burners. Covanta restarted the induced draft fan at 2020-11-20 13:56 and the forced draft fan at 2020-11-20 13:56. The natural gas burners were back online at 2020-11-20 14:10. The shutdown was completed at 2020-11-20 14:24.
Remedial Action Planned and/or Taken
Metro Vancouver’s facility operator Covanta is checking all relays and wiring associated with the induced draft to identify what is causing the induced draft fan to trip.
Gas burners unavailable and unable to close feed chute damper during shutdown
Unit | Duration | Date | Time
1 | 1 hr 2 min | 2020-09-29 | 00:08 - 01:10
Cause
Auxiliary burners on unit 1 were unavailable, due to a safety permissive, to maintain the secondary combustion zone temperature during a boiler shutdown period as required. The operator was unable to close the feed chute damper during the shutdown as required. Unit 1 was placed in shutdown mode at 2020-09-29 00:08 following an induced draft fan and forced draft fan trip. The operator was unable to close the feed chute damper as the refuse was above the damper in the feed chute. The Provincial Boiler Pressure Vessel Safety Act and the Provincial Gas Act required a boiler purge following the restart of the fans as the boiler temperature was below the safety permissive. The auxiliary burners were unavailable for a period of 18 minutes between 2020-09-29 00:08 and 2020-09-29 00:26.
Action Taken to Restore Steady State Conditions
Covanta restarted the induced draft fan at 2020-09-29 00:11 and the forced draft fan at 2020-09-29 00:12. The natural gas burners were back online at 2020-09-29 00:26. The shutdown was completed at 2020-09-29 01:10.
Remedial Action Planned and/or Taken
Metro Vancouver’s facility operator Covanta determined refuse quality contributed to unstable combustion. Covanta’s operators will continue to blend the refuse to ensure a more stable fuel quality.
Gas burners unavailable and unable to close feed chute damper during shutdown, Shutdown extended beyond 5 hours
Unit | Duration | Date/Time | Time
2 | 10 hr 14 min | 2020-08-23 | 05:29-15:43
Cause
The facility lost incoming power due to a BC Hydro outage. All three boilers were shut down utilizing the emergency backup power. Auxiliary burners on unit 2 were unavailable as the induced draft fan and the forced draft fan which are required for operation, are not powered during an emergency shutdown. The operator was unable to close the feed chute damper during the shutdown as required. Due to the extended power outage the shutdown period extended beyond 5 hours. Unit 2 was placed in shutdown mode at 2020-08-23 05:29 following the BC Hydro power trip. The operator was unable to close the feed chute damper as the refuse was above the damper in the feed chute. The Provincial Boiler Pressure Vessel Safety Act and the Provincial Gas Act required a boiler purge following the restart of the fans as the boiler temperature was below the safety permissive. The auxiliary burners were unavailable for a period of 8 hours and 41 minutes between 2020-08-23 05:29 and 2020-08-23 14:10.
Action Taken to Restore Steady State Conditions
Incoming power to the facility was restored at 2020-08-23 13:30 Covanta restarted the induced draft fan at 2020-08-23 13:45 and the forced draft fan at 2020-08-23 13:48. The natural gas burners were back online at 2020-08-23 14:10. The shutdown was completed at 2020-08-23 15:43.
Remedial Action Planned and/or Taken
None identified
Gas burners unavailable and unable to close feed chute damper during shutdown, Shutdown extended beyond 5 hours
Unit | Duration | Date/Time | Time
3 | 10 hr 23 min | 2020-08-23 | 05:29-15:52
Cause
The facility lost incoming power due to a BC Hydro outage. All three boilers were shut down utilizing the emergency backup power. Auxiliary burners on unit 3 were unavailable as the induced draft fan and the forced draft fan which are required for operation, are not powered during an emergency shutdown. The operator was unable to close the feed chute damper during the shutdown as required. Due to the extended power outage the shutdown period extended beyond 5 hours. Unit 3 was placed in shutdown mode at 2020-08-23 05:29 following the BC Hydro power trip. The operator was unable to close the feed chute damper as the refuse was above the damper in the feed chute. The Provincial Boiler Pressure Vessel Safety Act and the Provincial Gas Act required a boiler purge following the restart of the fans as the boiler temperature was below the safety permissive. The auxiliary burners were unavailable for a period of 9 hours and 27 minutes between 2020-08-23 05:29 and 2020-08-23 14:56.
Action Taken to Restore Steady State Conditions
Incoming power to the facility was restored at 2020-08-23 13:30 Covanta restarted the forced draft fan at 2020-08-23 13:40 and the induced draft fan at 2020-08-23 13:40. The natural gas burners were back online at 2020-08-23 14:56. The shutdown was completed at 2020-08-23 15:52.
Remedial Action Planned and/or Taken
None identified
Gas burners unavailable and unable to close feed chute damper during shutdown
Unit | Duration | Date/Time | Time
2 | 59 min | 2020-07-29 | 10:04-11:03
Cause
Auxiliary burners on unit 2 were unavailable, due to a safety permissive, to maintain the secondary combustion zone temperature during a boiler shutdown period as required. The operator was unable to close the feed chute damper during the shutdown as required. Unit 2 was placed in shutdown mode at 2020-07-29 10:04 following an induced draft fan and forced draft fan trip. The operator was unable to close the feed chute damper as the refuse was above the damper in the feed chute. The Provincial Boiler Pressure Vessel Safety Act and the Provincial Gas Act required a boiler purge following the restart of the fans as the boiler temperature was below the safety permissive. The auxiliary burners were unavailable for a period of 20 minutes between 2020-07-29 10:04 and 2020-07-29 10:24.
Action Taken to Restore Steady State Conditions
Covanta restarted the induced draft fan at 2020-07-29 10:05 and the forced draft fan at 2020-07-29 10:10. The natural gas burners were back online at 2020-07-29 10:24. The shutdown was completed at 2020-07-29 11:03.
Remedial Action Planned and/or Taken
Covanta is investigating the cause of the induced draft fan and forced draft fan trip.
Gas burners unavailable during shutdown and furnace temperature average below 800C
Unit | Duration | Date | Time
#1 | 56 minutes | 2021-03-28 | 15:29-16:25
Cause
Auxiliary burners on unit 1 were unavailable to maintain the secondary combustion zone temperature during boiler shutdown period. Unit 1 was placed in shutdown mode at 2021-03-28 15:29 due to a BC Hydro power outage. The Provincial Boiler Vessel Safety Act and the Provincial Gas Act require a boiler purge following the restart of the combustion fans. The auxiliary burners were unavailable for a period of 56 minutes between 2021-03-28 15:29 and 2021-03-28 16:25.
Action Taken to Restore Steady State Conditions
Covanta restarted the induced draft fan at 2021-03-28 15:31 and the forced draft fan at 15:32. The natural gas burners were back online at 2021-03-28 16:25. The shutdown was completed at 2021-03-28 17:11.
Remedial Action Planned and/or Taken
None
Gas burners unavailable during shutdown and furnace temperature average below 800C
Unit | Duration | Date | Time
#2 | 29 minutes | 2021-03-28 | 15:29-15:58
Cause
Auxiliary burners on unit 2 were unavailable to maintain the secondary combustion zone temperature during boiler shutdown period. Unit 2 was placed in shutdown mode at 2021-03-28 15:29 due to a BC Hydro power outage. The Provincial Boiler Vessel Safety Act and the Provincial Gas Act require a boiler purge following the restart of the combustion fans. The auxiliary burners were unavailable for a period of 29 minutes between 2021-03-28 15:29 and 2021-03-28 15:58.
Action Taken to Restore Steady State Conditions
Covanta restarted the induced draft fan and forced draft fan at 2021-03-28 15:35. The natural gas burners were back online at 2021-03-28 15:58. The shutdown was completed at 2021-03-28 16:43.
Remedial Action Planned and/or Taken
None
Gas burners unavailable during shutdown and furnace temperature average below 800C
Unit | Duration | Date | Time
#3 | 29 minutes | 2021-03-28 | 15:29-15:58
Cause
Auxiliary burners on unit 3 were unavailable to maintain the secondary combustion zone temperature during boiler shutdown period. Unit 3 was placed in shutdown mode at 2021-03-28 15:29 due to a BC Hydro power outage. The Provincial Boiler Vessel Safety Act and the Provincial Gas Act require a boiler purge following the restart of the combustion fans. The auxiliary burners were unavailable for a period of 29 minutes between 2021-03-28 15:29 and 2021-03-28 15:58.
Action Taken to Restore Steady State Conditions
Covanta restarted the induced draft fan at 2021-03-28 15:32 and the forced draft fan at 15:33. The natural gas burners were back online at 2021-03-28 15:48. The shutdown was completed at 2021-03-28 15:59.
Remedial Action Planned and/or Taken
None
3. CEMS Availability
| Required | Averaging | Monthly Availability
Analyzer | Availability | Period
| (% hours per quarter) |  | Unit 1 | Unit 2 | Unit 3
Opacity | 90 | Hour | 99.5 | 99.7 | 99.8
Oxygen | 90 | Hour | 99.4 | 97.5 | 97.5
CO | 90 | Hour | 99.4 | 97.5 | 97.5
SO2 | 90 | Hour | 99.4 | 97.5 | 97.5
NOx | 90 | Hour | 99.4 | 97.5 | 97.5
THC | 90 | Hour | 99.4 | 97.4 | 97.5
Stack Flow | 90 | Hour | 100 | 100 | 99.7
4. Shutdown Report
Unit 1
Duration in Hours |  | Reason |  |  | Date
0.8 |  | BC Hydro power interruption |  |  | 2023-06-04
0.2 |  | Poor refuse quality |  |  | 2023-05-08
70.47 |  | Annual minor maintenance outage
20.17 |  | Fabric filter bag replacement
1.07 |  | Induced draft fan trip
0.62 |  | Induced draft fan trip
0.43 |  | Induced draft fan trip
0.33 |  | Induced draft fan trip
1.22 |  | Induced draft fan trip
2.12 |  | Refuse crane failure
0.17 |  | Fabric filter bag replacement |  |  | 2023-05-09
0.42 |  | Tube inspection |  |  | 2023-05-10
15.25 |  | Feed water line repair
0.63 |  | Induced and forced draft fan trip
2.87 |  | Both refuse cranes out of service
2.15 |  | Both refuse cranes out of service
0.28 |  | High furnace pressure trip
0.12 |  | BC Hydro power interruption |  |  | 2023-06-24
Unit 2
Duration in Hours |  | Reason |  |  | Date
1.28 |  | BC Hydro power interruption |  |  | 2023-06-04
0.23 |  | Attemperator pump trip |  |  | 2023-06-10
0.8 |  | Ground fault trip |  |  | 2023-06-23
0.22 |  | BC Hydro power interruption |  |  | 2023-06-24
15.8 |  | Feed water line repair |  |  | 2022-04-26
0.38 |  | Induced draft fan trip |  |  | 2022-04-29
0.28 |  | Induced and forced draft fan trip |  |  | 2022-04-30
0.03 |  | Induced and forced draft fan trip |  |  | 2022-04-30
0.65 |  | Induced and forced draft fan trip |  |  | 2022-04-30
2.12 |  | Induced and forced draft fan trip |  |  | 2020-10-14
0.47 |  | BC Hydro power interruption |  |  | 2020-10-17
41.51 |  | Fabric filter bag replacement |  |  | October 19-21
0.47 |  | Turbine trip |  |  | 2020-10-23
0.35 |  | Turbine trip |  |  | 2020-10-23
1.12 |  | Turbine trip |  |  | 2020-10-24
0.18 |  | Turbine trip |  |  | 2020-10-26
0.2 |  | Capital works |  |  | 2020-10-27
27.88 |  | Boiler water wash |  |  | June 27-29
Unit 3
Duration in Hours |  | Reason |  |  | Date
0.67 |  | BC Hydro power interruption |  |  | 2023-06-04
51.02 |  | Fire in the grate drive area, repairs |  |  | June 9-11
1.52 |  | Fabric filter bag replacement |  |  | 2023-05-09
0.5 |  | Fabric filter bag replacement |  |  | 2023-05-10
0.87 |  | Fabric filter bag replacement |  |  | 2023-05-12
0.27 |  | BC Hydro power interruption |  |  | 2023-06-24
1.15 |  | Feed chute plug |  |  | 2021-01-23
0.68 |  | Feed chute plug |  |  | 2021-01-24
2.65 |  | Induced draft fan trip |  |  | 2021-01-25
0.23 |  | Forced draft fan trip |  |  | 2021-01-29
0.78 |  | Induced draft fan trip |  |  | 2020-07-28
2.4 |  | Induced draft fan trip |  |  | 2020-07-29
0.58 |  | Induced draft fan trip |  |  | 2020-07-29
1.5 |  | BC Hydro power interruption |  |  | 2021-12-26
14.37 |  | Boiler water wash |  |  | 2023-06-28
5. Facility Bypass and Emergency/spill Event Report
Date/Time | Cause |  |  |  | Duration
Action Taken
6. Other Data
|  |  | UNIT 1 | UNIT 2 | UNIT 3
Waste Received |  | tonnes | 21834.97
Waste Processed |  | tonnes/day | 248.38 | 216.69 | 223.18
Maximum Waste Processed |  | tonnes/day | 271.97 | 243.15 | 258.53
Units 1, 2, and 3
Natural Gas Consumed |  | m3/day | 1502.2733
|  | m3/month | 45068.2
Fly ash disposed |  | tonnes | 903.8
Bottom ash disposed |  | tonnes | 3946.17
7. Complaints and Responses
Date/Time | Complaint |  |  | Action Taken
#REF!